## 810782867 - Q&A Report
Safer Buildings Coalition UL 2524 Webinar (Begins at 2:00 minutes in)
Video Link: https://www.vimeo.com/298034062
Video Password: Available on SBC Site www.saferbuildings.org -> Webinars
Question Details
# | Question | Answer(s)
8 | While UL2524 is more for the active gear and the passive components are not included; is there any UL listing that simply suggest the passive gear is safe and free of fire and shock, so that AHJ not framiiar with DAS componets know these pieces are safe. | live answered: @ 1:00:00 synopsis: There is no listing of passive components at this point. The UL Codes and Regulatory Team regularly fields questions like that and can help guide AHJs. VISIT: https://www.ul.com/code-authorities/resources/regulatory-support/ | Featured Question and Answer:
1 | It's not clear in the Product Identity section what types of equipment are required to carry the UL 2524 listing. Can the panelists provide guidance? | See slide 20 & 21. 20: Scope: Cover products (e.g. repeater, transmitter, receiver, signal booster components, remote annunciators and operational consoles, power supply, and battery charging system components) used for in-building 2-way radio emergency radio communication enhancement systems installed in a location to improve wireless communication at that location. 21: Scope: Does not cover passive RF components which are defined in the standard as “any device that RF passes through that does not have an active electronic component that requires external power. This includes, antennas, splitters, couplers, coaxial cable and connectors. Passive components cannot amplify RF signals.”
2 | do fiber DAS active componants count? | live answered: Yes
3 | What's the difference between the 2 antenna indicators? | live answered
4 | Which UL locations are set up to perform UL-2524 certification - so we can confirm our overseas partners are using the correct facilities. | live answered: @ 56:52 Synopsis: The only two facilities that are geared for testing 2524 right now are in Long Island and Northbrook (USA), and the Toronto (Canada) facility. Other offices may be capable - send a request.
5 | Do you intend to certifiy intividual components or complete systems? | live answered: @ 57:51 Synopsis: We will certify individual components but they need to form a complete system.
6 | What is the difference between UL Listed and UL Certified? | live answered: @58:15 Synopsis: They are the same thing. Old terminology = Listed New terminology = Certified
7 | When unannounced visit to the mfg are performed, do you bring test any type equipment or is expected mfg have specific test equipment for testing? | live answered: @58:40 Synopsis: You may have some production line testing, UL will not be doing performance testing. Looking to verify product is built the same way
9 | Will other NRTL certified labs offer acceptable UL2524 testing or just UL? | Live Answered @ 1:04:26 Synopsis: UL does not have to do the testing. UL does not know if other NRTL labs will have the capability to do lab testing of UL 2524
11 | How will systems installed prior to UL2524 be identified? | live answered: @1:04:42 Synopsis: Prior to UL 2524 they would not have a listing mark. If they were certified under the Outline of Investigation, that would be identified in the online certification
13 | under requirement can you please clarify "modularity within same frequency band"? thanks! | live answered: @1:06:30 (Refer to slide 22) Synopsis: Modular means you can replace cards without the system being down for a long period of time.
14 | How is external filters defined? some external filter are optional for some particular application such as combining a commercial system and UHF applications. the external filters need to be in type 4 enclosure, so that belong to field inspection? | live answered: @ 1:07:45 Synopsis: Speaker conceded that filters need to be in Type 4 enclosures and that this would be inspected in the field. (Or, the OEM could incloude the filter in the system as optional)
15 | Do battery backup units require UL2524 certification if they are already UL50E certified? | live answered: @ 1:09:00 Synopsis: Yes, they require 2524 certification, because 50E only covers the enclosure.
16 | how do you define band? are you includeing 700 Band 14 and 700 Narrow band PSRS? as one band? | not answered: Will submit to panel and update doc later
17 | Field tunable UHF and VHF BDAs do exist. | Attendee Statement, not a question